## Overview
S.No | Domain | Responsible Person | Sensors | Parameters | Components | Application | O/P interface | Deployment Location | Proposed sensor deployment | No.Of sensors deployed | Deployment Status | No.Of sensors to be deployed | Data logging Frequency | Network interface | Packet formatiing protocol | Cost of Sensors | Cost of Network interface | Server
1 | Air Pollution | Dr.Sachin | Humidity |  | Nova PM SDS011: Measures PM2.5, PM10 DHT22: Measures Temperature and Humidity Groove Multichannel Gas Sensor: Measures CO, NO2 and NH3 concentrations (in PPM) | Measure the levels to identify the pollution level | Sensor analog data to node MCU (ardiuno ide) -ESP8266 board (microchip development board) wifi connects to Campus wifi or jio fi Dumped on the cloud via wifi??? | Indoors South Mess Kadamba Mess KCIS Washrooms Himalaya Washrooms Faculty Quarters 1 Faculty Quarters 2 Outdoors Nilgiri Football Ground KCIS Faculty Quarters Library Main Gate Bakul Nivas Felicity Ground Palash Nivas | 60 | 10 | • Sim card issue. ESIM modules without SIM are planned for the next 50 • CO sensors needs calibration • Gas based sensor calibration need to be planned • NH3 sensor functionality in toilets to be evaluated | 50 | Logged every 5 minutes The data is logged in a single container instance | LORAWAN is being planned | OneM2M (problems observed) |  |  | Thingspeak server –license for 50 channels each has8 words capacity
Temperature
PM 2.5 PM 10
CO
CO2
NH3
NO2
volatile organic content
2 | Class Ambience | Dr.Sachin | Temperature |  |  |  |  | Room 105
Light
AC Control
3 | Water Quality | Dr.Aftab | Ph, |  | DFRobot Gravity: Analog Turbidity Sensor DFRobot Gravity: Analog TDS Sensor DFRobot Gravity: Analog pH Sensor ESP32 WROOM 32D Power Reserve | Check pH in water tank | Sensor analog data to node MCU (ardiuno ide) -ESP32 board (microchip development board) wifi connects to Campus wifi or jio fi Dumped on the cloud via wifi | One water tank |  |  | • It was tested for one overhead tank • Data in place even after two months • Need to be deployed in more places |  | Logged every 5 minutes pH, TDS, Turbidity values Data logged into separate AEs | LORAWAN is being planned | OneM2M | 2k to 3k
|  |  | turbidity, |  |  | Check turbidity in water tank
|  |  | salinity(TDS), |  |  | Check Salinity of drinking water supply
|  |  | water level |  |  | Check water level in water tank
4 | Water Quantity | Dr.Aftab | water flow |  |  | Check water flow in pipes |  | Water level nodes are deployed in the Bakul Nivas Overhead tanks. |  |  | • Some are working but not calibrated • Some are not working • Selection has to be relooked into |  | Logged every 5 minutes Water level and flow values | LORAWAN is being planned | OneM2M | expensive
5 | Smart Energy meters | Dr.Aftab | Power usage |  |  |  | O/p connected via LORAWAN |  | 99 | 19 deployed in substation | Expected to work reliably | 80 to be installed after lockdown |  |  | OneM2M
6 | Smart Classroom | Mr.Prakash | Ultrasound and Light Sensors |  |  | classroom lighting and AC control | [8 empty] | OneM2M
[6 empty] | Projector lighting and volume control | [8 empty] | OneM2M
7 | Habitat Monitoring | Mr.Prakash | Accoustic sensors | Accoustic signatures |  | Habitat presence based on signatures | [8 empty] | OneM2M
8 | Mosquito corridor | Mr.Prakash | Micro Climatic Sensors | [11 empty] | OneM2M
9 | Crowd Counting | Mr.Prakash | Camera |  |  | crowd counting based on camera inputs and phone data interpolation | [8 empty] | OneM2M
10 | Road monitoring | Mr.Prakash & Dr. Jawahar | Camera |  |  | road monitoring with camera . • Road conditions • Road signage....street light assets • Road surface condition layer | [8 empty] | OneM2M
11 | Energy | Dr.Vishal Garg | Energy | Current voltage frequency power factor |  | Building energy efficiency demand response…..based on the requirement | Sum | Kohli building energy can be controlled presently |  |  |  |  | • Load monitoring 1/10th second to take action • Energy data is stored in every 15 minutes |  | OneM2M
Temperature
Humidity
12 | Washer Monitoring |  |  |  | EN8400 Energy Meter FS400A G1 Flow Meter ESP-32 Power Reserve |  |  | Bakul Nivas |  |  |  |  | Logged every 5 minutes The data is logged in a single container instance |  | OneM2M
13 | Soil moisture sensing

## Sensors & Communication
Category | Owner | Power Source | Sensor | Frequency | Sensor o/p Parameters | Names | Data types | units | Resolution | Geographical locations deployed | packet format | Node MCU | Node MCU i/f | Ist Stage Server | Ist Stage Server i/f | Server | Server i/f | Dashboard | Data to be displayed on dashboard | Remarks/Comments | Location
Power Distribution and consumption | Dr.Afthab | Mains | Crystal Energy meters(CT/Non CT) (PN: ) | Every 15 mts | a) Voltage & Current in each phase b) Power factor c) Frequency d) Power consumption (VA), Signed active power (KW), Signed reactive power (kVAr) e) Energy consumption f) Maximum demand(peak load) | a) V1,V2,V3, I1,I2,I3 b) PF c) F d) PVA,PKW,PkVAr e) EC f) MD | a) Float, 2 bytes, Voltage; Float, 2 bytes, Current b)Float, 1 bytes c)Float, 2 bytes d) Float, 4 bytes,Float, 4 bytes, ; Float, 4 bytes,; e) Float, 4 bytes f) Float, 2 bytes,; Float, 2 bytes, | a) Float, 2 bytes, Voltage; Float, 2 bytes, Current b)Float, 1 bytes c)Float, 2 bytes, Hz d) Float, 4 bytes, KVA; Float, 4 bytes, KW; Float, 4 bytes, KVAr; e) Float, 2 bytes, KW; Float, 2 bytes, KVA f)Float, 4 bytes, KWh |  | 100 19- in IIIT substation; 80 - as per existing meter installations; |  | NA | NA | Senra Server via Lorawan |  | OneM2M | fetch from senra server | fetch from OneM2M Server
Weather | Dr.Vishal | Mains with power backup | Hobo U30 S-THB-M002 (Humidity Sensor) S-TMB-M002 (Temperature Sensor) S-LIB-M003 (Solar radiation sensor) S-WCA-M003 (Wind speed sensor) S-WCA-M003 (Wind direction sensor) | As on now every 1 hour data is pumped to the hobo server Goal sensor data is available every minute for upto 24 hours for dynamic control and will be purged every 24 hours. Use 15 mt data is used for archiving | a. Time stamp b. Wind Direction c. Wind Speed d. Gust Speed e. Temperature f. Relative Humidity g. Solar Radiation h. Battery DC Voltage i. Rain(TBD) j. Pressure(TBD | a) TS b) WD c) WS d) GS e) T f) RH g) SR h) BDCV i) R(TBD) j) P(TBD) |  | a) Date Time, GMT+05:30 b) ϴ c) m/s d) m/s e) °C f) % g) W/m² h) V i) R(TBD) j) P(TBD) |  | 2 locations 1.Vindhya 2.On Top of Kohli bldg (new admin block) | NA | NA | NA | Hobo Server (cloud)??? | ethernet i/f | OneM2M | WiFi |  |  | data format cannot be changed at weather station
Pollution | Dr.Sachin | From Main supply | PM SDS011: Measures PM2.5, PM10 DHT22: Measures Temperature and Humidity Groove Multichannel Gas Sensor: Measures CO, NO2 and NH3 concentrations (in PPM) CO2 Sensor details needed??? | every 5mts | a) PM2.5, b) PM10 c) Temperature d) Humidity e) CO concentrations f) NO2 concentrations g) NH3 concentrations h)CO2 Concentration i)AQI what is AQI??? | a) PM2.5, b) PM10 c) T d) H e) CO f) NO2 g) NH3 h)CO2 |  | a)μg/m³ b) μg/m³ c) °C d) % e) ppm f) ppm g) ppm h) ppm | a)0.3μg/m³ b) 0.3μg/m³ c) 0.1°C d) 0.1 % e) ppm f) ppm g) ppm h) 1 ppm | Node 1 -AirVeda Node 2 - Main Gate Node 3 - Bakul Nivas Node 4 - FCYQ(Faculty Quarters) Node 5 - FLYG(Felicity Ground) Node 6 - FTBG(Football Ground) Node 7 - KCIS Node 8 - Library Node 9 -OBH(Palash Nivas) Node 10 -Nilgiri (not working) |  | ESP8266 | RS232/ i/o interface/I2C interface |  |  | ThingSpeak/ OneM2M | WiFi/JioFi | using thingspeak API data can be fetched |  | Calibration to be done at controller level or server level…??
Smart rooms with smart climate control(class rooms) HVAC (Heating, ventilation, and air conditioning)) | Dr.Vishal |  | T6713 - CO2 Sensor DHT22-Temp & humidity Bac net gate way(location mapping) watt node (energy data) hobo link ( weather data) B-one Hub T6713 - CO2 Sensor SHT21-Temp & humidity | data sent every 10mts | a) SR-CO2 Concentration b)SR- Temperatutre c) SR-Humidity | a) SRCO2 b) SRT c) SRH |  | a) ppm b) 0.1°C c) 0.1% |  | KCIS Room 105 (5 nodes) 15 |  | ESP32 WROOM 32D | i/o interface/I2C interface |  |  | ThingSpeak/ OneM2M | WiFi | Fetch from OneM2MServer |  | back net gate way(mapping) watt node (energy data) hobo link for weather data 72X16 AC data , when pumped to thingspeak server, problems are faced. | Room 105 Kohli block
Solar | Dr.Vishal |  |  |  | a) Voltage & Current in each phase b) Power factor c) Frequency d) Power consumption (VA), Signed active power (KW), Signed reactive power (kVAr) e) Energy consumption f) Maximum demand(peak load) | a) V1,V2,V3, I1,I2,I3 b) PF c) F d) PVA,PKW,PkVAr e) EC f) MD |  | a) V,C bValue c)Hz d) KVA; KW; KVAr; e) KW; KVA f) KWh |  | 5 |  | NA | NA | Senra Server via Lorawan |  | OneM2M | fetch from senra server |  |  | Here are the details of Nilgiri Roof Top Solar System. Total connected capacity on Nilgiri terrace is 200 KW. 3 inverters are connected, two are 80 KW (Growatt make) capacity which are connected to 174 KW capacity of solar panels And remaining one is 25 KW capacity inverter which is connected solar panels capacity is 26 KW. skycamera is on top of the new admin lab. since december not used images during mid noon is not reliable.density filter required for proper images. USB cable is used and presently it is not working. Tuesday prabhakar is planning to visiti and check skycamera is up with changed power supply Data is coming ok Growatt inverters data can obtain through app. the app details are as below: App name: Shine Phone ( available in google play store) Login details: IIIT HYD Pass word: 123456
Gate Monitoring: Finger printing,Face recognition FAStag reader | Mr.Prakash |  |  |  | a) GM Parameter 1 b) GM Parameter 2 c) GM Parameter 3 | a) GMP1 b) GMP2 c) GMP3 |  |  |  | 2 | [5 empty] | OneM2M | Wifi |  |  |  | Fastag reader
Smart Lamp post with Street lights On/OFF | Dr.Aftab |  |  |  | a) SL Parameter 1 b) SL Parameter 2 c) SL Parameter 3 | a) SLP1 b) SLP2 c) SLP3 |  |  |  | 10 |  | mallet board(transceiver i/f) ESP32 WROOM 32D(master) |  | virtual LORAWAN server account |  | OneM2M | fetch ( http) (mqtt format) |  |  |  | maingate to faculty quarters and in contiguous spaces
Water Distribution (Pump/Bores) | Dr.Sachin/DrAftab/Dr.Deepak | From Main supply/Power banks | DFRobot Gravity Analog pH Sensor Pro DFRobot Gravity Analog Turbidity Sensor DF Robot gravity: Analog TDS Sensor/meter for arduino HC-SR04-Ultrasonic Sensor |  | a) pH, b) Turbidity, c) Salinity(TDS), d) Water level and e) Water flow | a) pH, b) T, c) S, d) WL e) WF |  | a) Float, range: 0-14 b) Float, range: 0 to 10000, NTU c) Float, 40 to 2000, ppm (mg/L) d) Float, 20 to 400 cm | a) 0.0034 b) 2.44 c) 0.5 d) 0.3 | 4 Overhead tank deployments - 1. Bakul, 2. Parijaat, 3. Faculty Quarters, 4. Palash, ; 2-3 deployments in the sumps (Location TBD) a) pH -10, b) Turbidity -10, c) Salinity(TDS) 10, d) Water level -10 e) Water flow -20 |  | ESP32 WROOM 32D | Mostly Analog | NA |  | OneM2M | Wifi | Dashboard |  | fetch ( http) (mqtt format)
Crowd monitoring. Safety/Covid monitoring on Roads (social distancing,temperature/masks/women in distress) | Mr.Prakash |  |  | cameras and long range IR trippers Thermal camera | a) Camera Id, b) Geo location, c) Current people count, d) No. Of safe distance violations, e) No.Of mask violations, f) Url to live stream g) Url to latest snapshot, h) Time stamp_start i) Time stamp_end | a) CM_ID b) GEO_LOC c) CPC d) NSDV e) NMV f) ULS g) ULSPS, h) TSS i) TSE |  |  |  | 10 Main Entrance Area-1 Canteen Area down to the entrance point of Kohli block- 3 Main entrance Room 105 entrance Thub entrance Main Canteen-1 Near CIE -1 Near Nilgiri Block -1 Spare - 3 |  | PC(GPU) | LAN | [6 empty] | RF ID to be planned will be implemented with individual setup and dash board by december. Integration with master dashboard to be planned post december IR tripper count can be independently pushed on to the main dash board. Here is the link for MARG https://projects.kaiinos.com/marg/ Username : support@kaiinos.com Password : kaiinos Dream Vu video feed 15 frames / second analystics with the same speed camera specific 300-400$ PAL camera view 300mX300m alea camera 100mx100m NVIDEA nano for processing-GPU NBH,Canteens,Felicity ground,MAin gate,.....
Structural Health | Dr.Sachin\ Dr.Sunitha |  | 1. SCHENCK RoTec India Limited (details on India Mart website) Vibration Accelerometer Triaxial Sensor 2.DC Accelerometer Sensor, 3 Axis 3.Magnetic USB Accelerometer 4.*LVDTs*: (For measuring linear displacement) |  | a) SH Parameter 1 b) SH Parameter 2 c) SH Parameter 3 | a) SHP1 b) SHP2 c) SHP3 |  |  |  | 10 | [9 empty] | planned in the coming semster Support from Dr.Pradeep
OneM2M | [19 empty] | 2 thingspeak licenses ( 1 for smart city & 1 for sachin group) 50 channels(acc one node) and each has eight entries
Smart room control Modes
1.free cooling mode | AC switched off, Evaporative Cooler switched off off,exhaust vents open | Later on external AHUs to connected to Chilled water supply from Thub. It needs to be controlled and implement 3 modes. (infrastructure estimate 30L)
| 100% fresh air supply | Variable speed fan, AHU servicing,new evaporative pads and new pump). Exhaust damper control is also required
2.Evaporative cooling mode | AC switched off, Evaporative Cooler switched on,exhaust vents open
100% fresh air supply
3.Airconidtioning Mode | AC switched on, Evaporative Cooler switched off,exhaust vents partially open,Return air on | Present setup ok. With indoor ACs , presently.
| modulated fresh air supply depending on the requirement | It can be upgraded to AHU control later on
Smart room control Modes
AC options | internal AC or Later on external AHUs to connected to Chilled water supply from Thub. It needs to be controlled and implement 3 modes. (infrastructure estimate 30L) | [13 empty] | 1.free cooling mode | AC switched off, Evaporative Cooler switched off off,exhaust vents open 100% fresh air supply | Later on external AHUs to connected to Chilled water supply from Thub. It needs to be controlled and implement 3 modes. (infrastructure estimate 30L) Variable speed fan, AHU servicing,new evaporative pads and new pump). Exhaust damper control is also required
Number of students | based on camera or CO2 level or based on calendar or manual entry (25%/50%/75%/100%) | [13 empty] | 3.Airconidtioning Mode | AC switched on, Evaporative Cooler switched off,exhaust vents partially open,Return air on modulated fresh air supply depending on the requirement | Present setup ok. With indoor ACs , presently. It can be upgraded to AHU control later on
[15 empty] | AC options | internal AC or Later on external AHUs to connected to Chilled water supply from Thub. It needs to be controlled and implement 3 modes. (infrastructure estimate 30L)
[15 empty] | Number of students | based on camera or CO2 level or based on calendar or manual entry (25%/50%/75%/100%)
Controlling the lights using relays- to be decided
Controlling the AHUS, the pump on/off control,DAMPER on/OFF cotrol to close/open,control speed of motors for variable speed fans - to be worked on

## Pollution Deployment
S.No. | Buildings name | PM2.5 | PM10 | T | H | CO | NO2 | NH3 | CO2
1 | Vindhya
2 | Nilgiri | Yes | Yes | Yes | Yes
3 | Admin block, Himalaya range 'A' Block
4 | Kohli Research Block, Himalaya 'B' Block
5 | Bodh Bhavan,Himalaya 'C' Block
6 | T-Hub (Himalaya 'D' Block)
7 | Old Faculty Quarters
8 | Anand Nivas (Faculty & staff quarters)
9 | Budha Nivas (Faculty & staff quarters)
10 | Palash Nivas (Boys Hostel)
11 | Kadamba Nivas (Boys Hostel)
12 | Parijath Nivas (Girls Hostel)
13 | New women's Hostel-'A', 'B' & 'C' blocks
14 | Bakul Nivas (Boys Hostel) | Yes | Yes | Yes | Yes
15 | Sahana Atidhi Nivas (Guest House)
16 | Tarangani (Amphi Theatre)
17 | 11KV Substation
18 | Pump room-1 (at Main gate)
19 | Pump room-2 (at Sreenu canteen)
20 | Pump room-3 (at Bakul Nivas)
21 | Arogya centre
22 | Day Care centre
23 | Srujana Cultural centre
24 | Samskar School
25 | South mess at Palash Nivas
26 | North Mess at Palash Nivas
27 | Dining hall at Kadmaba Nivas
28 | Yutahar Mess
29 | Yoga Hall
30 | Main Gate | Yes | Yes | Yes | Yes
31 | FCYQ(Faculty Quarters) | Yes | Yes | Yes | Yes
32 | FLYG(Felicity Ground) | Yes | Yes | Yes | Yes
33 | FTBG(Football Ground) | Yes | Yes | Yes | Yes
34 | KCIS | Yes | Yes | Yes | Yes
35 | Library | Yes | Yes | Yes | Yes
36 | OBH | Yes | Yes | Yes | Yes

## Smart room deployment
KCIS AC Mapping
GROUND FLOOR
Name | Bacnet AC no.
FACULTY MEETING ROOM-1 | 0
FACULTY MEETING ROOM-2 | 1
FACULTY MEETING ROOM-3 | 2
FACULTY MEETING ROOM-4 | 3
RECEPTION AREA | 4
CEO ROOM | 5
BOARD ROOM | 6
CHAIR PERSON ROOM -1 | 7
CHAIR PERSON ROOM -2 | 8
FIRST FLOOR
WING-1
Name | Bacnet AC no.
STUDENT WORKSPACE | 14
F-1 | 13
F-2 | 12
F-3 | 11
WING-2
Name | Bacnet AC no.
STUDENT WORKSPACE | 25
MEETING ROOM -1 | 24
MEETING ROOM -2 | 23
F-4 | 20
F-5 | 21
F-6 | 22
WING-3
Name | Bacnet AC no.
STUDENT WORKSPACE | 37
F-7 | 36
F-8 | 35
F-9 | 34
F-10 | 33
WING-4
Name | Bacnet AC no.
STUDENT WORKSPACE | 49
MEETING ROOM | 48
F-11 | 47
F-12 | 46
F-13 | 45
SECOND FLOOR
WING-1
Name | Bacnet AC no.
F-14 | 17
F-15 | 16
F-16 | 15
STUDENT WORKSPACE-1 | 18
STUDENT WORKSPACE-2 | 19
WING-2
Name | Bacnet AC no.
F-17 | 26
F-18 | 27
F-19 | 28
F-20 | 29
F-21 | 30
STUDENT WORKSPACE | 32
MEETING ROOM | 31
WING-3
Name | Bacnet AC no.
STUDENT WORKSPACE -1 | 44
STUDENT WORKSPACE -2 | 43
F-24 | 42
F-23 | 41
F-24 | 40
F-25 | 39
F-26 | 38
WING-4
Name | Bacnet AC no.
F-29 | 50
F-28 | 51
F-27 | 52
MEETING ROOM -1 | 54
MEETING ROOM -2 | 53
STUDENT WORKSPACE | 55
THIRD FLOOR
WING-1
Name | Bacnet AC no.
STUDENT WORKSPACE 1 | 67
F-30 | 66
WING-2
Name | Bacnet AC no.
STUDENT WORKSPACE | 73
F-31 | 65
F-32 | 64
F-33 | 68
F-34 | 69
F-35 | 70
F-36 | 71
F-37 | 72
WING-3
Name | Bacnet AC no.
WING-4
Name | Bacnet AC no.
STUDENT WORKSPACE -1 | 84
STUDENT WORKSPACE -2 | 85
MEETING ROOM -AWAY | 82
MEETING ROOM -CLOSER | 83
F-38 | 78
F-39 | 79
F-40 | 80
F-41 | 81

## Room 105 deployment
ac | 4
projectors | 2
evaporative coolers
Lights
B-one Hub | 4 for Acs 2 for projectors
Smart room control Modes
1.free cooling mode | AC switched off, Evaporative Cooler switched off off,exhaust vents open 100% fresh air supply | Later on external AHUs to connected to Chilled water supply from Thub. It needs to be controlled and implement 3 modes. (infrastructure estimate 30L) Variable speed fan, AHU servicing,new evaporative pads and new pump). Exhaust damper control is also required
2.Evaporative cooling mode | AC switched off, Evaporative Cooler switched on,exhaust vents open 100% fresh air supply
3.Airconidtioning Mode | AC switched on, Evaporative Cooler switched off,exhaust vents partially open,Return air on modulated fresh air supply depending on the requirement | Present setup ok. With indoor ACs , presently. It can be upgraded to AHU control later on
AC options | internal AC or Later on external AHUs to connected to Chilled water supply from Thub. It needs to be controlled and implement 3 modes. (infrastructure estimate 30L)
Number of students | based on camera or CO2 level or based on calendar or manual entry (25%/50%/75%/100%)

## Water deployment
S.No. | Buildings name | TDS |  |  | Buildings name | pH |  |  | Buildings name | Turbidity |  |  | Buildings name | Water Level |  |  | Buildings name | Water Flow
|  | No.Of Deployments | Place | Water Source |  | No.Of Deployments | Place | Water Source |  | No.Of Deployments | Place | Water Source |  | No.Of Deployments | Place | Water Source |  | No.Of Deployments | S.No | Place | Water Source | Pipe size
1 | Vindhya | 5 | Sump and in 4 SS tanks after RO treatment | Manjeera | Vindhya |  |  |  | Vindhya |  |  |  | Vindhya |  |  |  | Vindhya | 1 | 13 | from P10 to vindhya | Borewater | 11/2" dia GI pipe
2 | Nilgiri | 1 | Sump | RO water inlet & outlet inlet common for bakul & Nilgiri | Nilgiri |  |  |  | Nilgiri |  |  |  | Nilgiri |  |  |  | Nilgiri
3 | Admin block, Himalaya range 'A' Block | 2 | Sump and in SS tank after RO treatment | Manjeera | Admin block, Himalaya range 'A' Block |  |  |  | Admin block, Himalaya range 'A' Block |  |  |  | Admin block, Himalaya range 'A' Block |  |  |  | Admin block, Himalaya range 'A' Block | 1 | 12 | From P10 to Himalaya Sump | Borewater | 11/2" dia GI pipe???
4 | Kohli Research Block, Himalaya 'B' Block |  |  |  | Kohli Research Block, Himalaya 'B' Block |  |  |  | Kohli Research Block, Himalaya 'B' Block |  |  |  | Kohli Research Block, Himalaya 'B' Block |  |  |  | Kohli Research Block, Himalaya 'B' Block
5 | Bodh Bhavan,Himalaya 'C' Block |  |  |  | Bodh Bhavan,Himalaya 'C' Block |  |  |  | Bodh Bhavan,Himalaya 'C' Block |  |  |  | Bodh Bhavan,Himalaya 'C' Block |  |  |  | Bodh Bhavan,Himalaya 'C' Block
6 | T-Hub (Himalaya 'D' Block) |  |  |  | T-Hub (Himalaya 'D' Block) |  |  |  | T-Hub (Himalaya 'D' Block) |  |  |  | T-Hub (Himalaya 'D' Block) |  |  |  | T-Hub (Himalaya 'D' Block)
7 | Anand Nivas (Faculty & staff quarters) | 1 | Sump | Manjeera - no treatment plants personal Ros | Anand Nivas (Faculty & staff quarters) | 1 | Overhead Tank |  | Anand Nivas (Faculty & staff quarters) | 1 | Overhead Tank |  | Anand Nivas (Faculty & staff quarters) | 1 | Overhead Tank |  | Anand Nivas (Faculty & staff quarters)
8 | Budha Nivas (Faculty & staff quarters) | 1 | Sump | Manjeera - no treatment plants personal Ros | Budha Nivas (Faculty & staff quarters) |  |  |  | Budha Nivas (Faculty & staff quarters) |  |  |  | Budha Nivas (Faculty & staff quarters) |  |  |  | Budha Nivas (Faculty & staff quarters)
11 | Palash Nivas (Boys Hostel) | 2 | Sump | Not occupied Main source RO RO water inlet & outlet | Palash Nivas (Boys Hostel) | 1 | Overhead Tank |  | Palash Nivas (Boys Hostel) | 1 | Overhead Tank |  | Palash Nivas (Boys Hostel) | 1 | Overhead Tank |  | Palash Nivas (Boys Hostel) | 1 | 8 | Frome Borewell P3 | Borewater | 2" dia GI pipe
12 | Kadamba Nivas (Boys Hostel) | 2 | Sump | RO water inlet & outlet | Kadamba Nivas (Boys Hostel) |  |  |  | Kadamba Nivas (Boys Hostel) |  |  |  | Kadamba Nivas (Boys Hostel) |  |  |  | Kadamba Nivas (Boys Hostel) | 1 | 15k | Frome Pumphouse 2 to Kadamba Nivas | Manjeera | 2" dia GI pipe
13 | Parijath Nivas (Girls Hostel) |  |  |  | Parijath Nivas (Girls Hostel) | 1 | Overhead Tank |  | Parijath Nivas (Girls Hostel) | 1 | Overhead Tank |  | Parijath Nivas (Girls Hostel) | 1 | Overhead Tank |  | Parijath Nivas (Girls Hostel) | 1 | 15p | Frome Pumphouse 2 to Kadamba Nivas | Manjeera | 2" dia GI pipe
14 | New women's Hostel-'A', 'B' & 'C' blocks | 2 | Sump | RO water inlet & outlet | New women's Hostel-'A', 'B' & 'C' blocks |  |  |  | New women's Hostel-'A', 'B' & 'C' blocks |  |  |  | New women's Hostel-'A', 'B' & 'C' blocks |  |  |  | New women's Hostel-'A', 'B' & 'C' blocks
15 | Bakul Nivas (Boys Hostel) | 2 | Sump | RO water inlet & outlet | Bakul Nivas (Boys Hostel) | 1 | Overhead Tank |  | Bakul Nivas (Boys Hostel) | 1 | Overhead Tank |  | Bakul Nivas (Boys Hostel) | 1 | Overhead Tank |  | Bakul Nivas (Boys Hostel)
16 | Sahana Atidhi Nivas (Guest House) |  |  | taken from Himalaya & Parijatha RO plants | Sahana Atidhi Nivas (Guest House) |  |  |  | Sahana Atidhi Nivas (Guest House) |  |  |  | Sahana Atidhi Nivas (Guest House) |  |  |  | Sahana Atidhi Nivas (Guest House) | 1 | 19 | From Himalaya to OFSQ and guest house |  | 2" dia delivery line
[18 empty] | 1 | 18 | From Himalaya & Parijath to guest house |  | 2" dia delivery line
17 | Old Faculty Quarters |  |  |  | Old Faculty Quarters |  |  |  | Old Faculty Quarters |  |  |  | Old Faculty Quarters |  |  |  | Old Faculty Quarters | 1 | 16 | From Himalaya & Parijath to OFSQ and guest house |  | 2" dia delivery line
[18 empty] | 1 | 17 | From Himalaya & Parijath to OFSQ |  | 2" dia delivery line
17 | Tarangani (Amphi Theatre) |  |  |  | Tarangani (Amphi Theatre) |  |  |  | Tarangani (Amphi Theatre) |  |  |  | Tarangani (Amphi Theatre) |  |  |  | Tarangani (Amphi Theatre)
18 | 11KV Substation |  |  |  | 11KV Substation |  |  |  | 11KV Substation |  |  |  | 11KV Substation |  |  |  | 11KV Substation
19 | Pump room-1 (at Main gate) | 1 | Sump | Manjeera | Pump room-1 (at Main gate) |  |  |  | Pump room-1 (at Main gate) |  |  |  | Pump room-1 (at Main gate) |  |  |  | Pump room-1 (at Main gate) | 1 | 1 | to hostels | Manjeera | 4" dia CI pipe
[18 empty] | 1 | 2 | to FSQ |  | 2" dia GI pipe
[18 empty] | 1 | 3 | to vindhya |  | 2" dia GI pipe
[18 empty] | 1 | 4 | to Himalaya |  | 2" dia GI pipe
[18 empty] | 1 | 5 | to FSQ |  | 2" dia GI pipe
[18 empty] | 1 | 6 | to pumphouse2 near vindhya canteen |  | 4" dia CI pipe
[18 empty] | 1 | 7 | to pumphouse4 near bakul Nivas |  | 4" dia CI pipe
20 | Pump room-2 (at Sreenu canteen) |  |  |  | Pump room-2 (at Sreenu canteen) |  |  |  | Pump room-2 (at Sreenu canteen) |  |  |  | Pump room-2 (at Sreenu canteen) |  |  |  | Pump room-2 (at Sreenu canteen) | 1 | 14 | From pumphouse to Vindhya | Borewater | 2" dia GI pipe
21 | Pump room-3 (at FSQ) |  |  |  | Pump room-3 (at Bakul Nivas) |  |  |  | Pump room-3 (at Bakul Nivas) |  |  |  | Pump room-3 (at Bakul Nivas) |  |  |  | Pump room-3 (at Bakul Nivas) | 1 | 9 | Frome Borewell P3 to Pumphouse 3 at FSQ | Borewater | 2" dia GI pipe
[18 empty] | 1 | 10m | From Pumphouse 3 at FSQ to Anand Nivas | Manjeera | 1 1/2" dia GI pipe
[18 empty] | 1 | 10b | From Pumphouse 3 at FSQ to Anand Nivas | Bore water | 2" dia GI pipe
[18 empty] | 1 | 11m | From Pumphouse 3 at FSQ to Budha Nivas | Manjeera | 1 1/2" dia GI pipe
[18 empty] | 1 | 11b | From Pumphouse 3 at FSQ to Budha Nivas | Bore water | 2" dia GI pipe
22 | Arogya centre |  |  |  | Arogya centre |  |  |  | Arogya centre |  |  |  | Arogya centre |  |  |  | Arogya centre
23 | Day Care centre |  |  |  | Day Care centre |  |  |  | Day Care centre |  |  |  | Day Care centre |  |  |  | Day Care centre
24 | Srujana Cultural centre |  |  |  | Srujana Cultural centre |  |  |  | Srujana Cultural centre |  |  |  | Srujana Cultural centre |  |  |  | Srujana Cultural centre
25 | Samskar School |  |  |  | Samskar School |  |  |  | Samskar School |  |  |  | Samskar School |  |  |  | Samskar School
26 | South mess at Palash Nivas |  |  |  | South mess at Palash Nivas |  |  |  | South mess at Palash Nivas |  |  |  | South mess at Palash Nivas |  |  |  | South mess at Palash Nivas
27 | North Mess at Palash Nivas |  |  |  | North Mess at Palash Nivas |  |  |  | North Mess at Palash Nivas |  |  |  | North Mess at Palash Nivas |  |  |  | North Mess at Palash Nivas
28 | Dining hall at Kadmaba Nivas |  |  |  | Dining hall at Kadmaba Nivas |  |  |  | Dining hall at Kadmaba Nivas |  |  |  | Dining hall at Kadmaba Nivas |  |  |  | Dining hall at Kadmaba Nivas
29 | Yutahar Mess |  |  |  | Yutahar Mess |  |  |  | Yutahar Mess |  |  |  | Yutahar Mess |  |  |  | Yutahar Mess
30 | Yoga Hall |  |  |  | Yoga Hall |  |  |  | Yoga Hall |  |  |  | Yoga Hall |  |  |  | Yoga Hall
| TBD | 6 |  | Sensors at functional borewater supply faculty quarters-1 Palash-1 Kadamba & newwomens hostel-1 Bakul Nivas-1 Vindhya-1 Himalaya-1 | TBD | 3 | Sumps |  | TBD | 3 |  |  | TBD | 3 |  |  | TBD
[6 empty] | 7 |  |  |  | 7 |  |  |  | 7 |  |  |  | 22
25
|  | TDS |  |  |  | pH |  |  |  | Turbidity |  |  |  | Water Level |  |  |  | water flow

## Power Distribution Deployment
S.No. | Buildings name
|  | No.Of CT Deployments | Location | No.Of Non CT Deployments
1 | Vindhya | 8 | CIE(Power) C3-SF | 12 | CIE (UPS) C3-FF /C3-SF/Th.F
|  |  | CIE(Power) C3-FF-AHU room |  | CIE (Lighting) C3-Th.F
|  |  | CIE (power) C5-FF-117 |  | CIE (Lighting) C5-Th.F
|  |  | CIE (Lighting) C5-FF -117 |  | SBH (Power) C7-FF
|  |  | CIE (Lighting) B6-FF |  | SBH (Lighting) C7-FF
|  |  | CIE (Power) B6-FF |  | Reliance Tower (C5-Cellar)
|  |  | CIE (Power) C3-Th.F-117 |  | CIE (UPS) C5/Th.F
|  |  | CIE (Power) C7-SF(SH3) |  | CIE (lighting) C3-SF
Airtel tower (at Substn.)
Hutch tower (at Substn.)
[5 empty] | Borewell Opp.to C4-Vindhya Block. | No specific CT ratio
St. lighting control at Vindhya.
2 | Nilgiri
|  | 7 | MSIT(FF) UPS-West wing | 4 | ACCESF(FF)Lighting, R-220
|  |  | MSIT (FF) Power(West) R-201 |  | Bakul.Ele.room (FF) DG supply
|  |  | ACCESF(FF) Power |  | Borewell opp. to Nilgiri block
|  |  | MSIT (FF) Power(East) |  | St. lighting control at Nilgiri bl.
MSIT (FF) Lighting(East)
Ups room, Nilgiri
Ups room, Nilgiri
3 | Admin block, Himalaya range 'A' Block |  |  | 4
Borewell East side Opp.to A-block
Openwell Sump at Himalaya `A`Block
Borewater motor to A block
Pumproom Sump at Himalaya `A`Block
4 | Kohli Research Block, Himalaya 'B' Block |  |  | 1 | Borewater motor to B block
5 | Bodh Bhavan,Himalaya 'C' Block* | 2
|  |  | Himalaya C block-Electrical room |  |  | El Measure energy meters are used???
Himalaya C block-Electrical room
6 | T-Hub (Himalaya 'D' Block)
7 | Anand Nivas (Faculty & staff quarters) | 1 |  | 1
|  |  | FSQ-Ananda Nivas |  | St. lighting control at FSQ
8 | Budha Nivas (Faculty & staff quarters) | 2
FSQ- Buddha Nivas
FSQ
11 | Palash Nivas (Boys Hostel) | 1
|  |  | Palash main(Power) Ele.room | 5 | Palash Nivas GF mess
Palash Nivas FF mess
Palash nivas East side borewell.
Palash nivas west side borewell.
Sump at OBH-Block
12 | Kadamba Nivas (Boys Hostel) | 2 |  | 1
|  |  | Kadamba (Cellar)Power |  | South side sump at NBH
Kadamba extn. (Cellar)Power
13 | Parijath Nivas (Girls Hostel) | 2
ParijjatNivas FF stairs
ParijjatNivas Extn FF stairs
14 | New women's Hostel-'A', 'B' & 'C' blocks |  |  | 1
Borewell Opp.to New Women`s hostel
15 | Bakul Nivas (Boys Hostel) | 2
Bakul Ele rooom (FF) Power-W
Bakul Ele rooom (FF) Power-E
16 | Sahana Atidhi Nivas (Guest House) | 1 |  | 2
|  |  | Sahana Athidi Nivas ele.room. |  | SBI- ATM at Pumproom-1
Guest house canteen
17 | Old Faculty Quarters
17 | Tarangani (Amphi Theatre) | 2
Tarangani Electrical room
Tarangani-Electrical room
18 | 11KV Substation | 2
Substation
Substation
19 | Pump room-1 (at Main gate) |  |  | 3
Pumproom No.1 at Main gate
Pumproom No.1 at Main gate
Pumproom No.1 at Main gate
20 | Pump room-2 (at Sreenu canteen/library) |  |  | 2
Openwell Pumproom No.2 at library
Pumproom No.2 at library
| Pump room-3 (at FSQ) |  |  | 4
Pumproom No.3 at FSQ
Pumproom No.3 at FSQ
Pumproom No.3 at FSQ
Pumproom No.3 at FSQ
21 | Pump room-4 (at Bakul Nivas) |  |  | 2
Pumproom-Pumproom No.4 at Bakul Nivas
Openwell Pumproom No.4 at Bakul Nivas
22 | Arogya centre |  |  | 1
Arogya center GF
23 | Day Care centre |  |  | 1
Daycare center GF
24 | Srujana Cultural centre |  |  | 1
Srujana cultural center GF
25 | Samskar School |  |  | 1
sanskar school.
26 | South mess at Palash Nivas
27 | North Mess at Palash Nivas
28 | Dining hall at Kadmaba Nivas |  |  | 1
Kadamba Mess FF
29 | Yuktahar Mess |  |  | 1
Yuktahar Mess SF
30 | Yoga Hall
31 | Substation* | 19 | LT panel |  |  | Indryn is installing the energy meters El measure company
Others
|  | 51 |  | 48

## Deployment
S.No. | Buildings name | Power Distribution and consumption | Weather | Pollution | Smart rooms with smart climate control | Solar | Gate Monitoring | Smart Lamp post with Street lights On/OFF | Water Distribution (Pump/Bores) | Crowd monitoring. | Structural Health
1 | Vindhya
2 | Nilgiri
3 | Admin block, Himalaya range 'A' Block
4 | Kohli Research Block, Himalaya 'B' Block
5 | Bodh Bhavan,Himalaya 'C' Block
6 | T-Hub (Himalaya 'D' Block)
7 | Old Faculty Quarters
8 | Anand Nivas (Faculty & staff quarters)
9 | Budha Nivas (Faculty & staff quarters)
10 | Palash Nivas (Boys Hostel)
11 | Kadamba Nivas (Boys Hostel)
12 | Parijath Nivas (Girls Hostel)
13 | New women's Hostel-'A', 'B' & 'C' blocks
14 | Bakul Nivas (Boys Hostel)
15 | Sahana Atidhi Nivas (Guest House)
16 | Tarangani (Amphi Theatre)
17 | 11KV Substation
18 | Pump room-1 (at Main gate)
19 | Pump room-2 (at Sreenu canteen)
20 | Pump room-3 (at Bakul Nivas)
21 | Arogya centre
22 | Day Care centre
23 | Srujana Cultural centre
24 | Samskar School
25 | South mess at Palash Nivas
26 | North Mess at Palash Nivas
27 | Dining hall at Kadmaba Nivas
28 | Yutahar Mess
29 | Yoga Hall

## WiFi
S.No. | Buildings name | No.Of WiFi Connections | Connections Required
1 | Vindhya_FF | 11
2 | Vindhya_SF | 15
3 | Vindhya_TF | 9
4 | Nilgiri_FF | 4
5 | Nilgiri_TF | 4
6 | Himalaya_GF | 3
7 | Himalaya_FF | 6
8 | Himalaya_SF | 6
9 | Admin block_UGF | 1
10 | Admin block_LGF | 1
11 | Admin block_FF | 8
12 | Admin block_SF | 2
13 | Maingate | 0 | 2
14 | faculty quarters | 0 | 6
15 | Substation | 0 | 2
16 | Bakul nivas roof top |  | 4
70